## General
General Parameters
Minimization objective | Cost
Number of hubs | 3
Interest rate (%) | 8
Maximum CO2 emissions (kg-CO2)
Big M | 100000
Note on A6: Rev: Leave blank if constraint is not imposed
Note on A7: Rev: Required; set sufficiently high for part load technology energy production, network energy exchanges, and storage exchanges. (BigM acts as an upper limit for Eout from part load technologies and network link exchanges, as well as Ein/Eout for storages.)

## Energy Carriers
List of Energy Carriers
Energy Carrier Name
elc
heat
gas
solar
oil
Note on A3: Rev: Case sensitive inputs

## Imports
Import Energy Carriers
Energy Carrier | Price (CHF/kWh) | CO2 (kg-CO2/kWh) | CO2 tax (CHF/kg-CO2) | Maximum supply (kWh)
gas | 0.09 | 0.198 | 0.01
solar
elc | 0.21 | 0.03
oil | 0.2 | 0.24 | 0.01
Note on A3: Rev: Entry must match an EC listed in "Energy Carriers" sheet
Note on E3: Rev: - insert value only if maximum supply constraint is imposed - applies to the total supply across all hubs

## Exports
Export Energy Carriers
Energy Carrier | Export Price (CHF/kWh)
elc | 0.1
Note on A3: Rev: Entry must match an EC listed in "Energy Carriers" sheet

## Demand
Energy Carrier Demand (kWh/h)
Energy Carrier | elc | heat | elc | heat | elc | heat
Hub | 1 | 1 | 2 | 2 | 3 | 3
Hour
1 | 3 | 21 | 4 | 22 | 5 | 23
2 | 3 | 24 | 4 | 25 | 5 | 26
3 | 3 | 26 | 4 | 27 | 5 | 28
4 | 3 | 28 | 4 | 29 | 5 | 30
5 | 3 | 30 | 4 | 31 | 5 | 32
6 | 3 | 31 | 4 | 32 | 5 | 33
7 | 24 | 73 | 25 | 74 | 26 | 75
8 | 23 | 66 | 24 | 67 | 25 | 68
9 | 24 | 63 | 25 | 64 | 26 | 65
10 | 19 | 58 | 20 | 59 | 21 | 60
11 | 19 | 49 | 20 | 50 | 21 | 51
12 | 19 | 37 | 20 | 38 | 21 | 39
13 | 23 | 30 | 24 | 31 | 25 | 32
14 | 23 | 27 | 24 | 28 | 25 | 29
15 | 23 | 26 | 24 | 27 | 25 | 28
16 | 24 | 32 | 25 | 33 | 26 | 34
17 | 22 | 31 | 23 | 32 | 24 | 33
18 | 22 | 39 | 23 | 40 | 24 | 41
19 | 27 | 39 | 28 | 40 | 29 | 41
20 | 28 | 40 | 29 | 41 | 30 | 42
21 | 27 | 44 | 28 | 45 | 29 | 46
22 | 10 | 44 | 11 | 45 | 12 | 46
23 | 12 | 14 | 13 | 15 | 14 | 16
24 | 11 | 18 | 12 | 19 | 13 | 20
25 | 3 | 20 | 4 | 21 | 5 | 22
26 | 3 | 23 | 4 | 24 | 5 | 25
27 | 3 | 25 | 4 | 26 | 5 | 27
28 | 3 | 27 | 4 | 28 | 5 | 29
29 | 3 | 29 | 4 | 30 | 5 | 31
30 | 3 | 40 | 4 | 41 | 5 | 42
31 | 24 | 82 | 25 | 83 | 26 | 84
32 | 24 | 70 | 25 | 71 | 26 | 72
33 | 23 | 65 | 24 | 66 | 25 | 67
34 | 19 | 58 | 20 | 59 | 21 | 60
35 | 19 | 49 | 20 | 50 | 21 | 51
36 | 19 | 37 | 20 | 38 | 21 | 39
37 | 23 | 30 | 24 | 31 | 25 | 32
38 | 23 | 27 | 24 | 28 | 25 | 29
39 | 23 | 24 | 24 | 25 | 25 | 26
40 | 23 | 30 | 24 | 31 | 25 | 32
41 | 22 | 29 | 23 | 30 | 24 | 31
42 | 22 | 41 | 23 | 42 | 24 | 43
43 | 28 | 33 | 29 | 34 | 30 | 35
44 | 27 | 37 | 28 | 38 | 29 | 39
45 | 27 | 42 | 28 | 43 | 29 | 44
46 | 26 | 40 | 27 | 41 | 28 | 42
47 | 25 | 38 | 26 | 39 | 27 | 40
48 | 20 | 36 | 21 | 37 | 22 | 38
Note on A3: Rev: - Entry must match an EC listed in "Energy Carriers" sheet
Note on A4: Rev: indicate only one hub ID per column
Note on A5: Rev: Must be consecutive hours; establishes the number of time periods in the model

## Energy Converters
Energy Converters
Process name --> | HP | Gas boiler-H1 | Gas boiler-H2 | Oil boiler | CHP gas | Solar thermal | PV
Capacity (kW) |  | 10
Investment cost (CHF/kW) | 1300 | 500 | 450 | 430 | 3000 | 1300 | 1800
Fixed O&M cost (CHF/kW) | 1.4 | 1.5 | 1.5 | 0.5 | 70 | 0.1 | 5
Variable O&M cost (CHF/kWh) | [6 empty] | 0.6
Input energy carrier | elc | gas | gas | oil | gas | solar | solar
Output energy carrier | heat | heat | heat | heat | elc, heat | heat | elc
Efficiency (%) | 400 | 95 | 95 | 85 | 30 | 55 | 19
Fixed input share
Fixed output share |  |  |  |  | 0.32, 0.68
Lifetime (years) | 15 | 15 | 15 | 15 | 15 | 15 | 20
Minimum load (%)
Solar specific power (kW/m2) | [5 empty] | 0.2 | 0.2
Maximum capacity (kW) | 5 |  | 40 | 80
Minimum capacity (kW) | [6 empty] | 5
Maximum output (kWh)
Minimum output (kWh)
CO2 investment (kg-CO2/kW)
Maximum capacity factor (%)
Minimum capacity factor (%)
Hubs | 1 | 1 | 2 | 3 | 1,2 | 1,3 | 1,3
Note on A3: Rev: - at least one technology must be provided - input values apply to each hub where technology is present
Note on A4: Rev: - pre-installed capacity (if any) - for multi-output techs with fixed output shares, capacity is defined with respect to first-listed output energy carrier
Note on A5: Rev: Does not apply to pre-installed capacities
Note on A7: Rev: Applied to the total energy output of a process
Note on A8: Rev: - required - separate multiple values with commas
Note on A9: Rev: - required - separate multiple values with commas
Note on A10: Rev: - for multi-output techs with fixed output shares, efficiency is defined with respect to first-listed output energy carrier
Note on A11: Rev: - insert values only if fixed input shares are required - comma separated values - must sum to one - must be equal to the number of input energy carriers - assumed to apply to ECs in the same order as provided in "Input energy carrier"
Note on A12: Rev: - insert values only if fixed output shares are required - comma separated values - must sum to one - must be equal to the number of output energy carriers - assumed to apply to ECs in the same order as provided in "Output energy carrier"
Note on A13: Rev: Required
Note on A14: Rev: Minimum load applies to first-listed output EC only for multi-output techs with fixed output shares. (Otherwise, minimum load applies to total output.)
Note on A15: Rev: Insert value for solar panel technologies only
Note on A16: Rev: Insert value only if max cap is imposed
Note on A17: Rev: Insert value only if minimum cap is imposed
Note on A18: Rev: - insert value only if max operation is imposed - total output over modeling horizon - applies to first-listed output EC only for multi-output techs with fixed output shares. Otherwise, applies to total output.
Note on A19: Rev: - insert value only if minimum operation is imposed - total output over modeling horizon - applies to first-listed output EC only for multi-output techs with fixed output shares. Otherwise, applies to total output.
Note on A20: Rev: Does not apply to pre-installed capacities
Note on A21: Rev: 100% unless otherwise specified
Note on A22: Rev: 0% unless otherwise specified
Note on A23: Rev: - required - comma separated values for multiple hubs

## Storage
Storage
Storage name --> | Battery | Heat Storage
Stored energy carrier | elc | heat
Capacity (kWh)
Investment cost (CHF/kWh) | 150 | 1
Fixed O&M cost (CHF/kWh)
Lifetime (years) | 10 | 15
Charging efficiency (%) | 90 | 90
Discharging efficiency (%) | 90 | 90
Maximum charging rate (%) | 30 | 30
Maximum discharging rate (%) | 30 | 30
Standby loss (%/hour) | 0.1 | 0.1
Minimum SoC (%)
Maximum capacity (kWh)
Minimum capacity (kWh)
CO2 investment (kg-CO2/kWh)
Hubs | 1,2,3 | 1,2,3
Note on A4: Rev: Required
Note on A5: Rev: pre-installed capacity (if any)
Note on A6: Rev: Does not apply to pre-installed capacities
Note on A8: Rev: Required
Note on A11: Rev: i.e., in each hour: stored energy <= charging rate * storage capacity
Note on A12: Rev: i.e., in each hour: discharged energy <= discharging rate * storage capacity
Note on A15: Rev: - per hub - insert value only if maxcap is imposed
Note on A16: Rev: - per hub - insert value only if minimum cap is imposed
Note on A17: Rev: Does not apply to pre-installed capacities
Note on A18: Rev: Required

## Network
Network Data
Node 1 | 1 | 2 | 3 | 1 | 2 | 3
Node 2 | 2 | 3 | 1 | 2 | 3 | 1
Length (m) | 100 | 150 | 150 | 100 | 150 | 150
Energy carrier | heat | heat | heat | elc | elc | elc
Network loss (%/m) | 0.1 | 0.06 | 0.06 | 0.09 | 0.065 | 0.065
Installed capacity (kW)
Maximum capacity (kW)
Minimum capacity (kW)
Investment cost (CHF/kW/m) | 1 | 1 | 1 | 0.9 | 0.9 | 0.9
Variable O&M cost (CHF/kWh)
Fixed O&M cost (CHF/kW)
Lifetime (years) | 50 | 50 | 50 | 55 | 55 | 55
CO2 investment (kg-CO2/kW/m)
Uni-directional flow? (Y)
Note on A7: Rev: total loss for network connection = loss/100 * length
Note on A11: Rev: Does not apply to pre-installed capacities
Note on A15: Rev: Does not apply to pre-installed capacities
Note on A16: Rev: - default: assumes bi-direction flow is possible - indicate "Y" only if uni-directional flow is enforced from Node 1 to 2

## Solar Profile
Solar Irradiation
Solar energy carrier: | solar
Hour | Irradiation (kW/m2)
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 0
8 | 0
9 | 0
10 | 0
11 | 0.056
12 | 0.192
13 | 0.324
14 | 0.38
15 | 0.324
16 | 0.189
17 | 0.037
18 | 0
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
25 | 0
26 | 0
27 | 0
28 | 0
29 | 0
30 | 0
31 | 0
32 | 0
33 | 0
34 | 0
35 | 0.056
36 | 0.194
37 | 0.327
38 | 0.383
39 | 0.328
40 | 0.192
41 | 0.039
42 | 0
43 | 0
44 | 0
45 | 0
46 | 0
47 | 0
48 | 0
Note on A5: Rev: Must match hourly profile given for demand data ("Demand" sheet)

## Imp Hr
Import Energy Carrier Price by Time Period (CHF/kWh)
Energy Carrier
Hour
Note on B3: Rev: Entry must match an EC listed in "Energy Carriers" and "Imports" sheets
Note on A4: Rev: Must match hourly profile given for demand data ("Demand" sheet)

## Exp Hr
Export Energy Carrier Price by Time Period (CHF/kWh)
Energy Carrier
Hour
Note on B3: Rev: Entry must match an EC listed in "Energy Carriers" and "Imports" sheets
Note on A4: Rev: Must match hourly profile given for demand data ("Demand" sheet)

## CF Hr
Capacity Factor by Time Period (%)
Energy Converter
Max/Min CF
Hour
Note on A1: Rev: Blank entries for capacity factor values for a given hour will be ignored
Note on A3: Rev: Entry must match an energy converter listed in "Energy Converters" sheet
Note on A4: Rev: Indicate "max" or "min" (case sensitive) to indicate maximum or minimum capacity factor for the specified hour, respectively
Note on A5: Rev: Discontinuos hours may be specified, but must be within the hourly range given for demand data (i.e., under the "Demand" sheet)

## Options
Objective (minimization)
Cost
Carbon